## READ ME
Attachment 2-1. READ ME
For use in the WQIP Annual Report's MS4 Outfall Discharge Assessments (WQIP Section 4.2.3), please fill in Jurisdictional Knowedge tabs with your jurisdictional follow up and knowledge regarding these outfalls.
Instructions for each tab
Identify Controllable Sources:
WHY: Per WQIP Section 4.2.3.1.1
WHAT: Requesting general knowledge of persistent and transient flow in your jurisdiction
HOW: In the yellow columns, describe what you learned from field screening, JRMP Annual Reporting, unnatural water balance HPWQC strategies, and/or any other strategies
Identify Sources of NALs Exceedances:
WHY: Per WQIP Section 4.2.3.1.3
WHAT: Requesting knowledge regarding the highest priority major MS4 outfalls that are in exceedance of NALs
HOW: In the yellow columns, describe sources contributing to NALs exceedances at the highest priority outfalls (WQIP Section 4.2.3.1.3). Sampled outfalls are provided in Appendix M. Potential sources are identified as check boxes in Column F. If possible, include the percent contribution of each source.
Persistent Flow % Contribution
WHY: Per WQIP Section 4.2.3.1.4
WHAT: Requesting % contribution from each known source at the major MS4 outfalls found to have persistent dry weather flows this monitoring year
HOW: In the yellow columns, if possible include the percent contribution of each source, if possible. Outfalls with persistent flow conditions are highlighted yellow.
Additional Resources:
To view field screening photos and field screenings from past monitoring years, filter for your jurisdiction at the below dashboard: Field Screening Dashboard

## Identify Controllable Sources
Attachment 2-5. Identify Controllable Sources
Identify Controllable Sources of Transient and Persistent Flows (WQIP Section 4.2.3.1.1.)
Information sources to describe controllable sources of transient and persistent Flows |  | Jurisdiction | Describe what you learned about known and suspected controllable sources (i.e., facilities, areas, land uses, and pollutant-generating activities) of transient and persistent flows | Describe sources of transient and persistent flows that have been reduced or eliminated | Identify any modifications of the field screening monitoring locations and frequencies to identify and eliminate sources of persistent flow non-stormwater discharges
Dry Weather MS4 Outfall Discharge Field Screening Data | -------------> | Laguna Hills | Field screening helps focus attention on areas with transient and persistent flows. | Sources have been difficult to identify based on the field screening data but most likely due to irrigation runoff and groundwater. | City staff has not made any modifications to its monitoring locations or inspection frequencies.
JRMP Annual Reports (facility inspections, responses to stormwater hotline calls and public complaints) | -------------> | Laguna Hills | The City's non-stormwater discharges typically originate from irrigation leaks, over-irrigation, or maintenance activities. | Facility inspections and responses to complaints help reduce flow from irrigations leaks, over irrigation and maintenance activities. | City staff has not made any modifications to its monitoring locations or inspection frequencies.
Data Obtained via Strategies (Outfall Capture Feasibility Studies, Flow Ecology Study, Inventory of Permitted Discharges and Water Impoundments)1 | -------------> | Laguna Hills | No conclusions have been reached about transient and persistent flows. | Unknown at this time. | City staff has not made any modifications to its monitoring locations or inspection frequencies.
Other (e.g. water district's rebate programs)2, 3 | -------------> | Laguna Hills | Water district rebate programs are provided and managed by Moulton Niguel Water District (MNWD) and El Toro Water District (ETWD). | Water disctrict landscape and irrigation rebate programs help to reduce flow from irrigation runoff. | N/A
1Inventory of Permitted Discharges and Water Impoundments
2SoCal Water Smart
3SoCal Water Smart Commercial
4 h2oc (Show Me My Watershed)

## Identify Sources of NALs Exceed
Attachment 2-5. Identify Sources of NALs Exceed
Identify Sources Contributing to NAL Exceedances at the Highest Priority Outfalls (WQIP Section 4.2.3.1.3)
Outfall Monitoring Data | [5 empty] | Outfall catchment percentages |  |  | Identify Sources Contributing to NAL Exceedances at the Highest Priority Major Outfalls |  | Identify Per Cent Contribution of Sources Contributing to NAL Exceedances at the Highest Priority Outfalls
Facility Identifier | Sampling Date | Jurisdiction | NAL Exceedance (sampled outfall) | Flow Condition | Sp. Conductivity (uS/cm) | Percent catchment in your jurisdiction | Jurisdiction of Discharge Point | Other jurisdictions within catchment | Identify Sources Contributing to NAL Exceedances at the Highest Priority Major Outfalls | Comments | Groundwater or tidal influence | Permitted Discharge: Reclaimed Water | Permitted Discharge: Potable Water | Irrigation Runoff: Reclaimed Water | Irrigation Runoff: Potable Water | Facility Discharge: Reclaimed Water | Facility Discharge: Potable Water | Illicit Connections | Unknown | Other
J06-10011-1 (J06P01) | 2024-05-29 10:44 | Laguna Hills | Fecal Coliform, Total Nitrogen, Manganese | Flowing | 3650 | 20.85 | Aliso Viejo | Laguna Woods, Lake Forest |  | The majority of the tributary area to this outfall is located in Laguna Woods and Lake Forest. Outfall Capture Feasibility Study water isotope testing conducted in 2019 identified that approximately 80% of outfall water is from groundwater sources. Sp. conductivity measurement of 3,650 us/cm continues to support finding that flow is influenced by groundwater. Fecal Coliform exceedance may be related to wildlife or pet waste and biofilm regrowth sources in the drainage area. Over application of nitrogen rich fertilizers for landscaping and the use of recycled water in the drainage area may have contributed to the Total Nitrogen exceedance whereas the Manganese exceedance may be influenced by groundwater sources. An investigation of the drainage area was conducted on 5/29/2024 coinciding with summer monitoring. Six non-stormwater flow observations were identified with one of the observations having a high flow rate. This discharge was determined to be from a health care facility's water softener. The facility was given a verbal warning and required to divert the wastewater discharge to the sanitary sewer. The other five observed non-stormwater flows were identified as being from over-irrigation. | 80 | [7 empty] | 20
J06-10011-1 (J06P01) | 2024-07-31 11:12 | Laguna Hills | Fecal Coliform, Total Nitrogen, Total Phosphorus, Manganese | Flowing | 3330 | 20.85 | Aliso Viejo | Laguna Woods, Lake Forest |  | The majority of the tributary area to this outfall is located in Laguna Woods and Lake Forest. Outfall Capture Feasibility Study water isotope testing conducted in 2019 identified that approximately 80% of outfall water is from groundwater sources. Sp. conductivity measurement of 3,330 us/cm continues to support finding that flow is influenced by groundwater. Fecal Coliform exceedance may be related to wildlife or pet waste and biofilm regrowth sources in the drainage area. Over application of nitrogen rich fertilizers for landscaping and the use of recycled water in the drainage area may have contributed to the Total Nitrogen exceedance whereas the Manganese exceedance may be influenced by groundwater sources. An investigation of the drainage area was conducted on 5/29/2024 coinciding with the first summer monitoring event. Six non-stormwater flow observations were identified with one of the observations having a high flow rate. This discharge was determined to be from a health care facility's water softener. The facility was given a verbal warning and required to divert the wastewater discharge to the sanitary sewer. The other five observed non-stormwater flows were identified as being from over-irrigation. | 80 | [7 empty] | 20
Fecal Coliform, Enterococci, Total Nitrogen, Total Phosphorous, Iron, Manganese
OCFS and or Flow Ecology Study found groundwater contributes to flow
CHWSRS sampling found HF183 presence
Comments in field screening noted curb run-off
Other (see comments)
Reclaimed water widely used in catchment
Illicit Connections
Permitted Discharge: Reclaimed
Permitted Discharge: Potable
Facility Discharge: Reclaimed
Irrigation Runoff: Reclaimed
Irrigation Runoff: Potable
Facility Discharge: Potable
Unknown
OCFS and or Flow Ecology Study found groundwater contributes to flow
CHWSRS sampling found HF183 presence
Comments in field screening noted curb run-off
Other (see comments)
Reclaimed water widely used in catchment
Illicit Connections
Permitted Discharge: Reclaimed
Permitted Discharge: Potable
Facility Discharge: Reclaimed
Irrigation Runoff: Reclaimed
Irrigation Runoff: Potable
Facility Discharge: Potable
Unknown

## PotentialSources (hidden)
Potential Sources
Reclaimed water widely used in catchment
Comments in field screening noted runoff
OCFS and or Flow Ecology Study found groundwater contributes to flow
CHWSRS sampling found HF183 presence
Permitted Discharge: Reclaimed Water
Permitted Discharge: Potable Water
Irrigation Runoff: Reclaimed Water
Irrigation Runoff: Potable Water
Facility Discharge: Reclaimed Water
Facility Discharge: Potable Water
Illicit Connections
Unknown
Other

## Persistent Flow % Contribution
Attachment 2-5. Persistent Flow % Contribution
Estimate the percent contritution from each known source for each MS4 outfall with persistent flow (WQIP Section 4.2.3.1.4). --------------->
Field Screening Observations | [26 empty] | Jurisdictional Knowledge
Facility Identifier | Jurisdiction | AvgDischarge (cfs, floating leaf) | Inspection Date | Flow Contribution | Flow Condition | Persistent Flow | Connectivity to Receiving Water | Priority (Appendix J) | PrioritizationScore | Sp. Conductivity (uS/cm) | Discharge (cfs, floating leaf) | Discharge (cfs, volumetric) | Discharge Trend | Scour Pond Water Condition | Dissipator Water Condition | Comments | Trash Condition | Trash Location | Dry MS4 Discharge Sampling (highest priority major outfall) | Wet MS4 Discharge Sampling (highest priority major outfall) | Outfall Capture Feasibility Study | Maintenance Issues | POINT_Y | POINT_X | SWN sensor location | Date Jurisdictional Manager contacted | Comments Describe what you found | Per cent Groundwater or tidal influence | Per cent Permitted Discharge: Reclaimed Water | Per cent Permitted Discharge: Potable Water | Per cent Irrigation Runoff: Reclaimed Water | Per cent Irrigation Runoff: Potable Water | Per cent Facility Discharge: Reclaimed Water | Per cent Facility Discharge: Potable Water | Percent Illicit Connections | Per cent Unknown | Per cent Other
J05-9800-2 | Laguna Hills | 0 | 2024-03-05 | Small Fraction (<10%) | Pooled or Ponded | Yes | Direct Connection | Not A Priority | NA | NA | NA | NA | Equal | Not present | Not present | NA | Not Present (0 Items) | NA | NA | NA | NA | Overgrown | 33.5892 | -117.7016 | Yes |  | Small drainage area to outfall including primary high-density residential. Field screening observation indicates access to outfall was blocked do to overgrown vegetation preventing an accurate flow estimate and measurement of conductivity. Based on the land uses in the drainage and groundwater influence found in other outfalls in the area it is suspected that runoff is comings from a combination of irrigation-runoff and groundwater sources. | [8 empty] | 100
J05-9800-2 | Laguna Hills | 0 | 2024-04-24 | NA | Pooled or Ponded | Yes | Direct Connection | Not A Priority | NA | NA | NA | NA | Equal | Not present | Not present | Vegetation blocking outfall causing ponding | Sparse (<10 Items) | Within area surrounding outfall | NA | NA | NA | Overgrown | 33.5892 | -117.7016 | Yes |  | Small drainage area to outfall including primary high-density residential. Field screening observation indicates access to outfall was blocked do to overgrown vegetation preventing an accurate flow estimate and measurement of conductivity. Based on the land uses in the drainage and groundwater influence found in other outfalls in the area it is suspected that runoff is comings from a combination of irrigation-runoff and groundwater sources. | [8 empty] | 100
J05-9255-1 (J05P01) | Laguna Hills | 0 | 2024-09-04 | NA | Pooled or Ponded | Yes | NA | Not A Priority | NA | NA | NA | NA | Equal | Not present | Not present | Viewed from a distance from wooden fence near sidewalk. Gate is blocked by large bush. | NA | NA | NA | NA | NA | NA | 33.5846 | -117.7064 |  |  | Drainage area to outfall includes high-density residential, single-family residential, and a water district's operation center. Field screening observation indicates access to outfall was blocked do to overgrown vegetation preventing an accurate flow estimate and measurement of conductivity. Based on the land uses in the drainage and groundwater influence found in other outfalls in the area it is suspected that runoff is comings from a combination of irrigation-runoff and groundwater sources. | [8 empty] | 100
J05-9800-2 | Laguna Hills | 0 | 2024-09-04 | NA | Pooled or Ponded | Yes | Partial - Significant Distance | Not A Priority | NA | NA | NA | NA | Equal | Not present | Not present | NA | Moderate (11-50 Items) | Within area surrounding outfall | NA | NA | NA | NA | 33.5892 | -117.7016 | Yes |  | Small drainage area to outfall including primary high-density residential. Field screening observation indicates access to outfall was blocked do to overgrown vegetation preventing an accurate flow estimate and measurement of conductivity. Based on the land uses in the drainage and groundwater influence found in other outfalls in the area it is suspected that runoff is comings from a combination of irrigation-runoff and groundwater sources. | [8 empty] | 100
J05-9271-6 | Laguna Hills | 0 | 2024-09-04 | NA | Pooled or Ponded | Unknown | None - Flow Infiltrates or Outfall is Dry | Not A Priority | NA | NA | NA | NA | Equal | Not present | Not present | NA | Sparse (<10 Items) | Within area surrounding outfall | NA | NA | NA | NA | 33.5873 | -117.7045 |  |  | Not evaluated - flow infiltrates.
J05-9255-1 (J05P01) | Laguna Hills | 0 | 2024-09-25 | NA | Pooled or Ponded | Yes | Undetermined | Not A Priority | NA | NA | NA | NA | Equal | Not present | Not present | Viewed ponding from sidewalk side of fence | Sparse (<10 Items) | Within area surrounding outfall | NA | NA | NA | NA | 33.5846 | -117.7064 |  |  | Drainage area to outfall includes high-density residential, single-family residential, and a water district's operation center. Field screening observation indicates access to outfall was blocked do to overgrown vegetation preventing an accurate flow estimate and measurement of conductivity. Based on the land uses in the drainage and groundwater influence found in other outfalls in the area it is suspected that runoff is comings from a combination of irrigation-runoff and groundwater sources. | [8 empty] | 100
J05-9271-6 | Laguna Hills | 0 | 2024-09-25 | NA | Dry | Unknown | NA | Not A Priority | NA | NA | NA | NA | Equal | Not present | Not present | NA | Sparse (<10 Items) | In flow path of outfall | NA | NA | NA | NA | 33.5873 | -117.7045 |  |  | Not evaluated - was dry.
J06-10011-1 (J06P01) | Laguna Hills | 0.60322 | 2024-03-05 | Major Fraction (>50%) | Flowing | Yes | Direct Connection | Priority | 98 | NA | NA | NA | Below Average Discharge | Not present | Not present | NA | Abundant (>50 Items) | Within area surrounding outfall | Yes | NA | 1 | None | 33.595 | -117.7158 | Yes |  | Outfall is located outside City's jurisdiction. A small portion of a commercial area within Laguna Hills near the 5 freeway is located above the outfall and may contribute flow. Most of the tributary area for this outfall is located in Laguna Woods Village in Laguna Woods, and in the City of Lake Forest. Outfall Capture Feasibility Study water isotope testing conducted in 2019 identified that approximately 80% of outfall water is from groundwater sources. Prior Sp. Conductivity measurements support that flow is influenced by groundwater. An investigation of the drainage area was conducted on 5/29/2024 coinciding with summer monitoring. Six non-stormwater flow observations were identified with one of the observations having a high flow rate. This discharge was determined to be from a health care facility's water softener. The facility was given a verbal warning and required to divert the wastewater discharge to the sanitary sewer. The other five observed non-stormwater flows were identified as being from over-irrigation. | 80 | [7 empty] | 20
J06-10011-1 (J06P01) | Laguna Hills | 0.60322 | 2024-05-29 | Major Fraction (>50%) | Flowing | Yes | Direct Connection | Priority | 98 | 3449 | 1.104 | NA | Below Average Discharge | Not present | Not present | NA | Moderate (11-50 Items) | In flow path of outfall | Yes | NA | 1 | NA | 33.595 | -117.7158 | Yes |  | Outfall is located outside City's jurisdiction. A small portion of a commercial area within Laguna Hills near the 5 freeway is located above the outfall and may contribute flow. Most of the tributary area for this outfall is located in Laguna Woods Village in Laguna Woods, and in the City of Lake Forest. Outfall Capture Feasibility Study water isotope testing conducted in 2019 identified that approximately 80% of outfall water is from groundwater sources. Sp. Conductivity measurement of 3,449 uS/cm supports that flow is influenced by groundwater. An investigation of the drainage area was conducted on 5/29/2024 coinciding with summer monitoring. Six non-stormwater flow observations were identified with one of the observations having a high flow rate. This discharge was determined to be from a health care facility's water softener. The facility was given a verbal warning and required to divert the wastewater discharge to the sanitary sewer. The other five observed non-stormwater flows were identified as being from over-irrigation. | 80 | [7 empty] | 20
J06-10011-1 (J06P01) | Laguna Hills | 0.60322 | 2024-07-31 | Major Fraction (>50%) | Flowing | Yes | Direct Connection | Priority | 98 | 3855 | 0.465 | NA | Below Average Discharge | Not present | Not present | Wet water mark | Abundant (>50 Items) | Within area surrounding outfall | Yes | NA | 1 | NA | 33.595 | -117.7158 | Yes |  | Outfall is located outside City's jurisdiction. A small portion of a commercial area within Laguna Hills near the 5 freeway is located above the outfall and may contribute flow. Most of the tributary area for this outfall is located in Laguna Woods Village in Laguna Woods, and in the City of Lake Forest. Outfall Capture Feasibility Study water isotope testing conducted in 2019 identified that approximately 80% of outfall water is from groundwater sources. Sp. Conductivity measurement of 3,855 uS/cm supports that flow is influenced by groundwater. | 80 | [7 empty] | 20
L03-708-11 (L03P05) | Laguna Hills | 0.12914 | 2024-05-13 | Small Fraction (<10%) | Flowing | Yes | Direct Connection | Priority | 48 | 3908 | 0.10286 | 0.028 | Below Average Discharge | Not present | Not present | Decaying algae, anoxic | Sparse (<10 Items) | Within area surrounding outfall | NA | Yes | NA | None | 33.5627 | -117.6759 |  |  | Outfall is located outside City's jurisdiction. However, the Nellie Gail estate residential community in the City is located above the outfall and may contribute flow to this outfall. Sp. conductivity measurement of 3,908 us/cm suggest flow is influenced by groundwater but there is not sufficient information available to calculate flow source percentages at this time. | [8 empty] | 100
L03-708-11 (L03P05) | Laguna Hills | 0.12914 | 2024-07-15 | Small Fraction (<10%) | Flowing | Yes | Direct Connection | Priority | 48 | 4520 | 0.036474 | 0.016 | Below Average Discharge | Not present | Not present | NA | Sparse (<10 Items) | In flow path of outfall | NA | Yes | NA | None | 33.5627 | -117.6759 |  |  | Outfall is located outside City's jurisdiction. However, the Nellie Gail estate residential community in the City is located above the outfall and may contribute flow to this outfall. Sp. conductivity measurement of 4,520 us/cm suggest flow is influenced by groundwater but there is not sufficient information available to calculate flow source percentages at this time. | [8 empty] | 100
*The storm water program manager was contacted on the following dates: 7/29/2024 with a reminder of water quality sampling. An update for the MS4 program was provided at a WQIP meeting on 4/22/2024, 6/24/2024, and 8/26/2024.